## Distribution Costs and Plans
GRC Distribution Pipeline General Costs and Plans Information |  | Notes
Most Recent GRC proceeding name | Test Year 2019 GRC | An alternate unit and cost data version is presented in the 2019/2020/2021 RSAR reports filed with the CPUC.
Most Recent GRC proceeding number | A.17-10-007/-008 (cons.)
Most Recent GRC proceeding years covered, starting with test year | 2019-2023
Open or Upcoming GRC proceeding name if any | Test Year 2024 GRC
Open or Upcoming GRC proceeding number if any | N/A
Open or Upcoming GRC proceeding years covered, starting with test year | 2024-2027
Total distribution main miles owned by the utility | 8247 | EOY 2021 DOT Report
Total distribution service miles owned by the utility | 7068 | EOY 2021 DOT Report
Average length of service pipeline (miles per service) | 54 | EOY 2021 DOT Report
Total distribution main pipeline miles to be replaced per year | N/A | Historical miles of mains replaced for 2019 to 2021: 2019 = 32miles, 2020 = 31miles, 2021 = 37miles We do not forecast TOTAL main replacement. 2024 GRC forecast for years 2022-2024 for Steel Replacements are 9.8, 9.8, and 9.8 miles respectively. For non-state of the art plastic forecast is 54, 56, and 60 miles for 2022-2024. We do not have a forecast for 2025 and 2026.
Total distribution service pipeline miles to be replaced per year | n/a | Historical miles of services replaced for 2019 to 2021: 2019 = 33miles, 2020 = 32miles, 2021 = 44miles. For 2022-2026, we do not forecast services to be replaced.
Total distribution main pipeline miles to be added per year | N/A | Historical miles of mains added for 2019 to 2021: 2020= 7.1 miles 2021= 7.2 miles 2022 to 2026 we do not forecast miles of pipe to be added per year.
Total distribution service pipeline miles to be added per year | n/a | Historical miles of services added for 2019 to 2021: 2019 = 25.5 miles 2020= 10.4 miles 2021= 7.3 miles 2022 to 2026 we do not forecast miles of service pipe to be added per year.
Number of new regulator stations to be built during GRC period | 1 | 1 known new reg station for 3 roots development
Number of regulator stations to be replaced during GRC period | 5 | based on 1 actual per year 2019-2021, 1 per year forecast through 2022-2023
Number of regulator stations to be repaired/upgraded during GRC period | 5 | based on 1 actual per year 2019-2021, 1 per year forecast through 2022-2023
Average cost per mile to replace distribution pipeline (mains and services) | 1253137.92 | Average of RAMP ($261/ft) and DIMP ($213.92/ft) GRC unit costs of feet of distribution pipeline replacements
Average cost per mile to replace distribution main pipeline | 1253137.92 | Average of RAMP ($261/ft) and DIMP ($213.92/ft) GRC unit costs of feet of distribution pipeline replacements
Average cost per mile to replace distribution service pipeline | 1253137.92 | Average of RAMP ($261/ft) and DIMP ($213.92/ft) GRC unit costs of feet of distribution pipeline replacements
Average cost per mile to replace distribution main pipeline with diameter of 2” or less | n/a | Cost is not tracked by pipeline size. The diameter of a pipeline directly effects the average cost/mile to replace the pipeline. As a pipeline diameter gets larger, the width of the pipe gets larger requiring more trench construction. The requirements for depth of the pipe, under federal and state regulations, changes from service pipe to main pipe increasing the cost per mile. Larger trench activity requires additional work in completing the trench and necessary street repair following the pipe installation increasing the cost. Generally the cost of the pipe itself is a minor portion of the entire installation cost and less than 10% of the total cost.
Average cost per mile to replace distribution main pipeline with diameter over 2” through 4” | n/a | Cost is not tracked by pipeline size
Average cost per mile to replace distribution main pipeline with diameter over 4” through 8” | n/a | Cost is not tracked by pipeline size
Average cost per mile to replace distribution main pipeline with diameter over 8” through 12” | n/a | Cost is not tracked by pipeline size
Average cost per mile to replace distribution pipeline with diameter over 12” | n/a | Cost is not tracked by pipeline size
Average cost per mile to install new distribution main pipeline | 1253137.92 | Average of RAMP ($261/ft) and DIMP ($213.92/ft) GRC unit costs of feet of distribution pipeline replacements
Average cost per mile to install new distribution service pipeline | 1253137.92 | Average of RAMP ($261/ft) and DIMP ($213.92/ft) GRC unit costs of feet of distribution pipeline replacements
Average cost of new regulator station or regulator station replacement | 490239.67 | average of Reg Station installs during current GRC Period
Average cost of regulator station repair/upgrade (excluding whole station replacement) | $134.63/Hr | Repairs to a regulator station can vary widely from $100 to hundreds of thousands of dollars depending on what amount of work is required. Therefore limited information can be drawn from an average for this activity. If a specific repair cost is required, SDG&E can provide an average for that repair.
Total gas distribution system costs per year | (2019) $109.0, (2020) $147.3, (2021) $176.7 | SDG&E sum of Gas Capital and O&M distribution system costs for the years indicated, in millions of 2021 dollars.
Total gas distribution system costs per distribution mains and services pipeline miles per year | $11,508/mile (2021 O&M+CAP dollars divided by 2021 Main & Service mileage) | SDG&E sum of Gas Capital and O&M distribution system costs added together divided by mileage from 2021 DOT report. 8,247 miles of main, 7,081 miles of Service based on average ft of 54' per service. Total=15,328 Miles. Total 2021 Costs (O&M+CAP)=176.7M. $$/miles = 11,508

## Program Specific
GRC Distribution System Plans and Risks Information by Replacement Program
Program Information | Program Name | Pipeline Program Total | Vintage Integrity Plastic Plan |  | RAMP Main and Service Replacements | General Notes & Assumptions
| Program Goal |  | Program and tool developed and managed as part of the DIMP which is used to prioritize risk mitigation on early vintage plastic. Plastic pipe manufactured and used for gas service from the 1960s through the early 1980s exhibits a brittle-like cracking characteristic that could cause a leak to grow and release additional natural gas than would otherwise be released. |  | Replace vintage Stl based on risk rankings
| Main Program Data Source |  | Data is collected through operational maintenance and inspection activities, primarily though the completion of leak repair orders. GIS is primarily used to utilized to identify pipeline attribute information and to create the relationships between the leak records and pipeline assets. |  | GIS is primary data source, combined with leak records.
| Materials of Pipelines Covered by Program |  | Early vintage plastic manufactured by Dupont with the moniker Aldyl-A. |  | Steel Mains and Services
| Ages of Pipelines Covered by Program |  | Installed from 1969 to 1985 |  | Steel mains and services installed before 1934, Steel mains and services installed after 1934
| Program Includes Mains, Services or Both? |  | Mains and associated services |  | both
Planning Period | [5 empty] | A replacement project list is never completed, it is ongoing and projects are selected on a priority basis. The length of time for a project from proposed to completed differs with every project. Can range from immediate (one week) to several years, depending on many factors.
Program Forecasts | Pipelines Miles with Known Locations to be Replaced by Program During Years Covered by Most Recent GRC, Per Year |  | 2019 - 27 miles of mains and associated services |  | 2019-2023, 29.39 miles of main and services per year | Pipelines both mains and services are replaced all over the SDG&E service territory as needed. Replacement mileages for "known locations" for major projects involving replacement of non-state of the art plastic pipe (DIMP projects) can be shown from the recent GRC years. This non-state of the art plastic pipe is forecast to be replaced at the following levels (miles): 2021 - 52 2022 - 54 2023 - 56 2024 - 60 Other: 2022-2023 - 1.1 mile - Adobe Falls Steel 6" High Pressure Pipeline Relocation
| Pipelines Miles with Locations Yet to be Determined to be Replaced by Program During Years Covered by Most Recent GRC, Per Year |  | N/A |  | n/a | Miles to be replaced are identified by the planning team based on most current risk results in the several months preceding the start of a given year. As specified in most recent GRC (2019), for TY2019 replacements: Early Vintage Steel (7.4 miles); Pre-1933 threaded steel main (14.8 miles);
| Total Pipeline Miles or Count of Regulator Stations to be Replaced by Program During Years Covered by Most Recent GRC, Per Year |  | N/A |  | n/a | Regulator station replacements are not part of Vintage Integrity Plastic Plan
| Total Pipeline Miles to be Replaced by Program for Program Completion, If Applicable |  | Need for replacement is determined based on risk results. |  | based on risk score, part of GRC
| Total Pipeline Miles Subject to Program |  | 1624 |  | Stl mains and services within SDGE territory | EOY 2021 DOT Report. Note: There was no regulator replacement "program" in the 2019 GRC. Typically SDG&E replaces from 2 to 5 regulator stations per year.
| Expected Year of Program Completion Per Utility’s Goals, If Applicable |  | N/A |  | n/a | Need for replacement is determined based on risk results.
Calculated Probability of Leak per Year, or Risk of Failure | Minimum Possible |  | N/A |  | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| Maximum Possible |  | N/A |  | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| Minimum |  | 0.0053925 | Leaks per mile-year | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| 25th Percentile |  | 0.019681 | Leaks per mile-year | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| Average |  | 0.027896 | Leaks per mile-year | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| 75th Percentile |  | 0.04003 | Leaks per mile-year | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| 95th Percentile |  | 0.10143 | Leaks per mile-year | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| Maximum |  | 44.1389 | Leaks per mile-year | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
Calculated Probability of Serious Safety Incident Given Leak, | Minimum Possible |  | N/A |  | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| Maximum Possible |  | N/A |  | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| Minimum |  | 0.00021084 | Serious incidents per leak | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| 25th Percentile |  | 0.00035769 | Serious incidents per leak | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| Average |  | 0.00036789 | Serious incidents per leak | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
| 75th Percentile |  | 0.00038015 | Serious incidents per leak | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
or Consequence | 95th Percentile |  | 0.00041274 | Serious incidents per leak | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
of Failure | Maximum |  | 0.00041683 | Serious incidents per leak | N/A, SDG&E does not calculate leak rates or failure rates nor safety consequences associated with assets or programs.
Risk Score | Minimum Possible Risk Score |  | N/A |  | n/a, a singular risk score for the category in column "A" does not exist
| Maximum Possible Risk Score |  | N/A |  | n/a, a singular risk score for the category in column "A" does not exist
| Minimum Risk Score |  | 1.94e-06 | Serious incidents per mile-year | n/a, a singular risk score for the category in column "A" does not exist
| 25th Percentile Risk Score |  | 7.3e-06 | Serious incidents per mile-year | n/a, a singular risk score for the category in column "A" does not exist
| Average Risk Score |  | 1.035e-05 | Serious incidents per mile-year | n/a, a singular risk score for the category in column "A" does not exist
| 75th Percentile Risk Score |  | 1.475e-05 | Serious incidents per mile-year | n/a, a singular risk score for the category in column "A" does not exist
| 95th Percentile Risk Score |  | 3.702e-05 | Serious incidents per mile-year | n/a, a singular risk score for the category in column "A" does not exist
| Maximum Risk Score |  | 0.016808 | Serious incidents per mile-year | n/a, a singular risk score for the category in column "A" does not exist
| Risk Score Value at Which Prioritized in Most Recent GRC |  | N/A |  | n/a, a singular risk score for the category in column "A" does not exist
| Risk Score Value at Which Immediate Action Taken, If Any |  | N/A |  | n/a, a singular risk score for the category in column "A" does not exist
Risk Scoring Discussion and Further Information | Aspects Contributing to Risk of Failure |  | A quantitative risk model is utilized to determine the probability of a leak and its associated consequence for material and construction threats on vintage plastic medium pressure mains. The probability of failure is determined by gradient boosted decision tree model using (but not limited to) internal asset data, historical leak data, and publicly available data. |  | n/a, a singular risk score for the category in column "A" does not exist
| Aspects Contributing to Consequences of Failure |  | The consequence of failure is determined by modeling the probability that a leak is hazardous, followed by the probability that the hazardous leak results in life-safety consequences using a gradient boosted decision tree and statistical model. Internal and external data considered in the consequence model includes (but not limited to) historical leak data, internal asset data, location, and PHMSA gas distribution incident data. |  | n/a, a singular risk score for the category in column "A" does not exist
| Discussion of Risk Scoring Approach |  | A quantitative risk assessment method is utilized to determine the probability of a leak, the probability that a leak is hazardous, and the probability of a serious incident given a leak for material and construction threats on vintage plastic medium pressure mains. Medium pressure mains are those with operating pressure of 60 psig or less. The risk of failure is defined as the probability of a serious incident per year. |  | n/a, a singular risk score for the category in column "A" does not exist
| Staff Contact Name and Email | Doug White, dwhite1@sdge.com
New Question: Include columns reflecting all distribution pipeline or regulator station repair or replacement, by cost code (MAT) or by program, whichever is more narrow. | Response: There are hundreds of repairs made on pipelines and regulator stations annually. We have approx 500 regulator stations that are inspected annually and many will have repairs. We have over 15,000 miles of pipelines, which will have repairs ranging from small pipe wrap repairs to large repairs with pipe replacements. This question needs to be more specific to provide the information required.
New Question: If forecasts are not available, provide historical data based on 2019-2021. | Response: All the rows in the "Program-Specific" section that involve forecasts, have already had the historical data for 2019 - 2021 submitted in the data rows in this submittal.

## Customer Data
Confidential and Protected Material pursuant to PUC Section 583, GO 66-D, D.17-09-023
Customer Data | Response | Notes & Assumptions
Total customers | 953916 | Total Customers from Q4 Gas Summary Statistics - Consumption Data By Zip Code
Average annual daily core consumption (MMcfd) | 103.9081 | Sum of Core Load Q4 Gas Summary Statistics - Consumption Data By Zip Code divided by 10,000
Average annual daily noncore consumption (MMcfd) | CONFIDENTIAL | Sum of NC Load from Q4 Gas Summary Statistics - Consumption Data By Zip Code divided by 10,000
Average annual daily wholesale consumption (MMcfd) | 0 | No wholesale customers in SDG&E territory
Average annual daily company use and lost/unaccounted for gas (MMcfd) | 0 | Unknown
Systemwide peak hour (date and hour) | 2021-01-25 20:00 | Queried the hourly data for the SoCalGas-to-SDG&E-transfer meters
Average annual daily core consumption metered hourly (MMcfd) | 5.7 | Queried the hourly data for the SoCalGas-to-SDG&E-transfer meters and the SDG&E noncore meters and then subtracted the difference for core hourly data
Average annual daily noncore consumption metered hourly (MMcfd) | CONFIDENTIAL | Queried the hourly data for the SDG&E noncore meters
Average annual daily company use and lost/unaccounted for gas metered hourly (MMcfd) | 0 | Unknown
Average annual daily wholesale consumption metered hourly (MMcfd) | 0 | N/A
Core consumption during peak hour, for core metered hourly (MMcfh) | 17.9 | Queried the hourly data for the transfer meters and the noncore meters for the Peak Day & Hour and then subtracted the difference for core hourly data
Noncore consumption during peak hour, for noncore metered hourly (MMcfh) | CONFIDENTIAL | Queried the hourly data for the noncore meters during the Peak Day And Hour
Wholesale consumption during peak hour, for wholesale metered hourly (MMcfh) | 0 | No wholesale customers in SDG&E territory
Company use and lost/unaccounted for gas during peak hour, for wholesale metered hourly (MMcfh) | 0 | Unknown
Estimated core consumption during peak hour, for core not metered hourly (MMcfh)* | 0 | Unknown
Estimated noncore consumption during peak hour, for noncore not metered hourly (MMcfh) | 0 | Unknown
Estimated wholesale consumption during peak hour, for other not metered hourly (MMcfh) | 0 | Unknown
Estimated other consumption during peak hour, for other not metered hourly (MMcfh) | 0 | Unknown